## 2015 Summary (for web)
Parameter | Ontario Maximum Acceptable Concentration (MAC) | Units | Lab's Method Detection Limit (MDL) | Measured Concentrations |  |  | MAC Exceedance (Y/N)
2015
REGULATED INORGANICS
Antimony | 6 | µg/L | 0.02 | 0.08 | - | 0.15 | No
Arsenic | 25 | µg/L | 0.2 | 0.4 | - | 0.6 | No
Barium | 1000 | µg/L | 0.02 | 14.6 | - | 23.2 | No
Boron | 5000 | µg/L | 0.2 | 13.5 | - | 17.5 | No
Cadmium | 5 | µg/L | 0.003 | 0.003 | - | 0.009 | No
Chromium | 50 | µg/L | 0.03 | 0.08 | - | 0.1 | No
Fluoride* | 1.5 | mg/L | 0.06 | 0.06 | - | 0.83 | No
Free Chlorine Residual | 4 | mg/L | N/A | 0.2 | - | 1.2 | No
Mercury | 1 | µg/L | 0.01 | <MDL |  |  | No
Selenium | 10 | µg/L | 0.04 | 0.16 | - | 0.19 | No
Sodium | 20 | mg/L | 0.01 | 10.2 | - | 17 | No
Uranium | 20 | µg/L | 0.002 | 0.032 | - | 0.036 | No
*Fluoride injection at the Elgin Water Treatment Plant was offline for maintenance between Oct. 28 - Dec. 2, 2015
Parameter | Ontario Maximum Acceptable Concentration (MAC) | Units | Lab's Method Detection Limit (MDL) | Measured Concentrations |  |  | MAC Exceedance (Y/N)
2015
REGULATED ORGANICS
Alachlor | 5 | µg/L | 0.02 | <MDL |  |  | No
Aldicarb | 9 | µg/L | 0.01 | <MDL |  |  | No
Aldrin + Dieldrin | 0.7 | µg/L | 0.01 | <MDL |  |  | No
(Aldrin) | -- | µg/L | 0.01 | <MDL |  |  | No
(Dieldrin) | -- | µg/L | 0.01 | <MDL |  |  | No
Atrazine | -- | µg/L | 0.01 | 0.06 | - | 0.08 | No
Atrazine + N-dealkylated metabolites | 5 | µg/L | 0.01 | 0.08 | - | 0.11 | No
Azinphos-methyl | 20 | µg/L | 0.05 | <MDL |  |  | No
Bendiocarb | 40 | µg/L | 0.01 | <MDL |  |  | No
Benzene | 5 | µg/L | 0.32 | <MDL |  |  | No
Benzo(a)pyrene | 0.01 | µg/L | 0.004 | <MDL |  |  | No
Bromoxynil | 5 | µg/L | 0.33 | <MDL |  |  | No
Carbaryl | 90 | µg/L | 0.05 | <MDL |  |  | No
Carbofuran | 90 | µg/L | 0.01 | <MDL |  |  | No
Carbon tetrachloride | 5 | µg/L | 0.16 | <MDL |  |  | No
Chlordane (Total) | 7 | µg/L | 0.01 | <MDL |  |  | No
(a-chlordane) | -- | µg/L | 0.01 | <MDL |  |  | No
(g-chlordane) | -- | µg/L | 0.01 | <MDL |  |  | No
(oxychlordane) | -- | µg/L | 0.01 | <MDL |  |  | No
Chlorpyrifos | 90 | µg/L | 0.02 | <MDL |  |  | No
Cyanazine | 10 | µg/L | 0.03 | <MDL |  |  | No
Diazinon | 20 | µg/L | 0.02 | <MDL |  |  | No
Dicamba | 120 | µg/L | 0.2 | <MDL |  |  | No
1,2-Dichlorobenzene | 200 | µg/L | 0.41 | <MDL |  |  | No
1,4-Dichlorobenzene | 5 | µg/L | 0.36 | <MDL |  |  | No
DDT + Metabolites | 30 | µg/L | 0.01 | <MDL |  |  | No
(op-DDT) | -- | µg/L | 0.01 | <MDL |  |  | No
(pp-DDD) | -- | µg/L | 0.01 | <MDL |  |  | No
(pp-DDE) | -- | µg/L | 0.01 | <MDL |  |  | No
(pp-DDT) | -- | µg/L | 0.01 | <MDL |  |  | No
1,2-Dichloroethane | 5 | µg/L | 0.35 | <MDL |  |  | No
1,1-Dichloroethylene | 14 | µg/L | 0.33 | <MDL |  |  | No
Dichloromethane | 50 | µg/L | 0.35 | <MDL |  |  | No
Parameter | Ontario Maximum Acceptable Concentration (MAC) | Units | Lab's Method Detection Limit (MDL) | Measured Concentrations |  |  | MAC Exceedance (Y/N)
2015
REGULATED ORGANICS CONTINUED
2,4-dichlorophenol | 900 | µg/L | 0.15 | <MDL |  |  | No
2,4-D | 100 | µg/L | 0.19 | <MDL |  |  | No
Diclofop-methyl | 9 | µg/L | 0.4 | <MDL |  |  | No
Dimethoate | 20 | µg/L | 0.03 | <MDL |  |  | No
Dinoseb | 10 | µg/L | 0.36 | <MDL |  |  | No
Diquat | 70 | µg/L | 1 | <MDL |  |  | No
Diuron | 150 | µg/L | 0.03 | <MDL |  |  | No
Glyphosate | 280 | µg/L | 1 | <MDL |  |  | No
Heptachlor + Heptachlor Epoxide | 3 | µg/L | 0.01 | <MDL |  |  | No
(heptachlor) | -- | µg/L | 0.01 | <MDL |  |  | No
(heptachlor epoxide) | -- | µg/L | 0.01 | <MDL |  |  | No
Lindane (Total) | 4 | µg/L | 0.01 | <MDL |  |  | No
Malathion | 190 | µg/L | 0.02 | <MDL |  |  | No
Methoxychlor | 900 | µg/L | 0.01 | <MDL |  |  | No
Metolachlor | 50 | µg/L | 0.01 | 0.03 | - | 0.06 | No
Metribuzin | 80 | µg/L | 0.02 | <MDL |  |  | No
Monochlorobenzene | 80 | µg/L | 0.3 | <MDL |  |  | No
Paraquat | 10 | µg/L | 1 | <MDL |  |  | No
Parathion | 50 | µg/L | 0.02 | <MDL |  |  | No
Pentachlorophenol | 60 | µg/L | 0.15 | <MDL |  |  | No
Phorate | 2 | µg/L | 0.01 | <MDL |  |  | No
Picloram | 190 | µg/L | 1 | <MDL |  |  | No
Polychlorinated Biphenyls (PCBs) | 3 | µg/L | 0.04 | <MDL |  |  | No
Prometryne | 1 | µg/L | 0.03 | <MDL |  |  | No
Simazine | 10 | µg/L | 0.01 | <MDL |  |  | No
Temephos | 280 | µg/L | 0.01 | <MDL |  |  | No
Terbufos | 1 | µg/L | 0.01 | <MDL |  |  | No
2,3,4,6-tetrachlorophenol | 100 | µg/L | 0.2 | <MDL |  |  | No
Triallate | 230 | µg/L | 0.01 | <MDL |  |  | No
Trichloroethylene | 50 | µg/L | 0.44 | <MDL |  |  | No
2,4,6-trichlorophenol | 5 | µg/L | 0.25 | <MDL |  |  | No
2,4,5-T | 280 | µg/L | 0.22 | <MDL |  |  | No
Trifluralin | 45 | µg/L | 0.02 | <MDL |  |  | No
Vinyl Chloride | 2 | µg/L | 0.17 | <MDL |  |  | No
Parameter | Ontario Maximum Acceptable Concentration (MAC) | Units | Lab's Method Detection Limit (MDL) | Measured Concentrations |  |  | MAC Exceedance (Y/N)
2015
NITRATES
Nitrate (as nitrogen) | 10 | mg/L | 0.006 | 0.061 | - | 0.776 | No
Nitrate + Nitrite (as nitrogen) | 10 | mg/L | 0.006 | 0.061 | - | 0.776 | No
Nitrite (as nitrogen) | 1 | mg/L | 0.003 | <MDL |  |  | No
Parameter | Ontario Maximum Acceptable Concentration (MAC) | Units | Lab's Method Detection Limit (MDL) | Measured Concentrations |  |  | MAC Exceedance (Y/N)
2015
TRIHALOMETHANES
Trihalomethanes (total) | 100 | µg/L | 0.37 | 17 | - | 38 | No
Bromoform | -- | µg/L | 0.34 | <MDL |  |  | No
Chloroform | -- | µg/L | 0.29 | 8.7 | - | 23 | No
Dibromochloromethane | -- | µg/L | 0.37 | 1.4 | - | 4.2 | No
Bromodichloromethane | -- | µg/L | 0.26 | 5.3 | - | 10 | No
Parameter | Ontario Maximum Acceptable Concentration (MAC) | Units | Lab's Method Detection Limit (MDL) | Measured Concentrations |  |  | MAC Exceedance (Y/N)
2015
MICROBIOLOGICAL
E. coli | 0 | cfu/100 mL | 0 | 0 | - | 2 | Yes
Total Coliform | 0 | cfu/100 mL | 0 | 0 | - | 1040 | Yes
Heterotrophic Plate Count | N/A | cfu/1 mL | 10 | 10 | - | 2000 | No
Parameter | Ontario Maximum Acceptable Concentration (MAC) | Units | Lab's Method Detection Limit (MDL) | Measured Concentrations |  |  | MAC Exceedance (Y/N)
2015
NON-REGULATED INORGANICS/ORGANICS
Alkalinity | N/A | mg/L | 2 | 81 | - | 97 | No
Aluminum | N/A | µg/L | 0.3 | 31.7 | - | 37.4 | No
Ammonia+Ammonium (N) | N/A | mg/L | 0.04 | <MDL |  |  | No
Calcium | N/A | mg/L | 0.02 | 27.3 | - | 33.1 | No
Chloride | N/A | mg/L | 0.04 | 9.2 | - | 18 | No
Cobalt | N/A | µg/L | 0.004 | 0.005 | - | 0.014 | No
Colour | N/A | TCU | 3 | <MDL |  |  | No
Conductivity | N/A | uS/cm | 2 | 249 | - | 324 | No
Copper | N/A | mg/L | 0.002 | 0.002 | - | 0.026 | No
Cyanide | 0.2 | mg/L | 0.002 | <MDL |  |  | No
1,1 Dichloroethene | 14 | µg/L | 0.33 | <MDL |  |  | No
De-ethylated atrazine | N/A | µg/L | 0.01 | 0.02 | - | 0.03 | No
Dissolved Organic Carbon | N/A | mg/L | 0.2 | <MDL |  |  | No
Ethylbenzene | N/A | µg/L | 0.33 | <MDL |  |  | No
Hardness | N/A | mg/L | 0.05 | 101 | - | 119 | No
Iron | N/A | µg/L | 2 | 3 | - | 5 | No
Langelier Index | N/A | N/A | N/A | -0.05 | - | 0.1 | No
m/p-xylene | N/A | µg/L | 0.43 | <MDL |  |  | No
Magnesium | N/A | mg/L | 0.003 | 7.94 | - | 8.92 | No
Manganese | N/A | µg/L | 0.01 | 0.04 | - | 0.39 | No
Nickel | N/A | µg/L | 0.1 | 0.3 | - | 0.6 | No
Nitrogen-Kjeldahl (N) | N/A | mg/L | 0.05 | <MDL |  |  | No
Organic Nitrogen | N/A | mg/L | 0.05 | <MDL |  |  | No
o-xylene | N/A | µg/L | 0.17 | <MDL |  |  | No
pH | N/A | pH units | 0.05 | 8.2 | - | 8.21 | No
Potassium | N/A | mg/L | 0.002 | 0.998 | - | 1.48 | No
Silica | N/A | mg/L | 0.04 | 0.81 | - | 1.77 | No
Silver | N/A | µg/L | 0.002 | 0.022 | - | 0.04 | No
Solids (Total Dissolved) | N/A | mg/L | 30 | 140 | - | 166 | No
Sulphate | N/A | mg/L | 0.04 | 27 | - | 34 | No
Sulphide | N/A | mg/L | 0.006 | <MDL |  |  | No
Tetrachloroethene | 30 | µg/L | 0.35 | <MDL |  |  | No
Toluene | N/A | µg/L | 0.36 | <MDL |  |  | No
Total Chlorine | N/A | mg/L | N/A | 0.8 | - | 1.01 | No
Total Phosphorus | N/A | mg/L | 0.003 | <MDL |  |  | No
Toxaphene | N/A | µg/L | 5 | <MDL |  |  | No
2,4,5-TP (Silvex) | N/A | µg/L | 0.18 | <MDL |  |  | No
Turbidity | 1 | NTU | 0.1 | <MDL |  |  | No
Xylene; total | 300 | µg/L | 0.43 | <MDL |  |  | No
Zinc | N/A | µg/L | 2 | <MDL |  |  | No